## Sampling Schedule
Expected Sampling Start Date | 2020-06-29
[9 empty] | Skipdays | Reason
SampleID Configuration: "Parameter-Location (abbreviated)-sample day" | [8 empty] | 2020-07-02 | July 4th Observation
[9 empty] | 2020-07-03 | July 4th Observation
[9 empty] | 2020-07-06 | July 4th Observation
Day | Sampling Dates | Time | Parameter | Sampling Location | Value | Value2 | Units | SampleID | Contracting Party | Notes | Discard | Detection | Duplicate Variance | Duplicate Variance 2 | Parameter (units)
1 | 2020-06-29 | 10:40 | cBOD | Plant Influent | 150 |  | mg/L | cBOD-PI-01 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | cBOD (mg/L)
1 | 2020-06-29 | 9:40 | cBOD | Primary Effluent | 210 |  | mg/L | cBOD-PE-01 | NYEnvironmental | samples from trough No.2 (4th from the ending) |  |  |  |  | cBOD (mg/L)
1 | 2020-06-29 | 8:50 | cBOD | Final Tank Effluent | 4.3 |  | mg/L | cBOD-FTE-01 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | cBOD (mg/L)
1 | 2020-06-29 | 8:00 | cBOD | CCT Effluent | 5.7 |  | mg/L | cBOD-CCTE-01 | NYEnvironmental | from small access hole at North end of the CCT's |  |  |  |  | cBOD (mg/L)
1 | 2020-06-29 | 10:40 | Enterococcus | Plant Influent | 2737500 |  | MPN/100mL | EC-PI-01 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | Enterococcus (MPN/100mL)
1 | 2020-06-29 | 10:40 | pH | Plant Influent | 6.86 |  | - | pH-PI-01 | MDE | Samples from screen No.3(last from exit door) Outside of QA/QC limits |  |  |  | Potential Outlier | pH (-)
1 | 2020-06-29 | 10:40 | Temperature | Plant Influent | 26.9 |  | C | T-PI-01 | MDE | Samples from screen No.3(last from exit door) |  |  |  |  | Temperature (C)
1 | 2020-06-29 | 10:40 | Field TRC | Plant Influent | 0.22 |  | mg/L | FTRC-PI-01 | MDE | Samples from screen No.3(last from exit door) |  |  |  |  | Field TRC (mg/L)
1 | 2020-06-29 | 9:40 | Enterococcus | Primary Effluent | 706800 |  | MPN/100mL | EC-PE-01 | NYEnvironmental | samples from trough No.2 (4th from the ending) |  |  |  |  | Enterococcus (MPN/100mL)
1 | 2020-06-29 | 8:50 | Enterococcus | Final Tank Effluent | 217600 |  | MPN/100mL | EC-FTE-01 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
1 | 2020-06-29 | 8:00 | Enterococcus | CCT Effluent | 910 |  | MPN/100mL | EC-CCTE-01 | NYEnvironmental | from small access hole at North end of the CCT's Not typical of CCT Effluent |  |  |  | Potential Outlier | Enterococcus (MPN/100mL)
1 | 2020-06-29 | 8:50 | Enterococcus | Final Tank Effluent | 217600 |  | MPN/100mL | EC-FTE-01 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
1 | 2020-06-29 | 10:40 | Fecal Coliform | Plant Influent | 4150000 |  | MPN/100mL | FC-PI-01 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | Fecal Coliform (MPN/100mL)
1 | 2020-06-29 | 9:40 | pH | Primary Effluent | 6.88 |  | - | pH-PE-01 | MDE | samples from trough No.2 (4th from the ending) Outside of QA/QC limits |  |  |  | Potential Outlier | pH (-)
1 | 2020-06-29 | 9:40 | Temperature | Primary Effluent | 26.4 |  | C | T-PE-01 | MDE | samples from trough No.2 (4th from the ending) |  |  |  |  | Temperature (C)
1 | 2020-06-29 | 9:40 | Field TRC | Primary Effluent | 0.01 |  | mg/L | FTRC-PE-01 | MDE | samples from trough No.2 (4th from the ending) |  |  |  |  | Field TRC (mg/L)
1 | 2020-06-29 | 9:40 | Fecal Coliform | Primary Effluent | 12100000 |  | MPN/100mL | FC-PE-01 | NYEnvironmental | samples from trough No.2 (4th from the ending) |  |  |  |  | Fecal Coliform (MPN/100mL)
1 | 2020-06-29 | 8:50 | Fecal Coliform | Final Tank Effluent | 866000 |  | MPN/100mL | FC-FTE-01 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | Fecal Coliform (MPN/100mL)
1 | 2020-06-29 | 8:00 | Fecal Coliform | CCT Effluent | 75 |  | MPN/100mL | FC-CCTE-01 | NYEnvironmental | from small access hole at North end of the CCT's |  |  |  |  | Fecal Coliform (MPN/100mL)
1 | 2020-06-29 | 8:50 | Fecal Coliform | Final Tank Effluent | 1140000 |  | MPN/100mL | FC-FTE-01 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | Fecal Coliform (MPN/100mL)
1 | 2020-06-29 | 8:50 | pH | Final Tank Effluent | 7.14 |  | - | pH-FTE-01 | MDE | samples from last channels/final tank Outside of QA/QC limits |  |  |  | Potential Outlier | pH (-)
1 | 2020-06-29 | 8:50 | Temperature | Final Tank Effluent | 26.4 |  | C | T-FTE-01 | MDE | samples from last channels/final tank |  |  |  |  | Temperature (C)
1 | 2020-06-29 | 8:50 | Field TRC | Final Tank Effluent | 0 |  | mg/L | FTRC-FTE-01 | MDE | samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
1 | 2020-06-29 | 10:40 | TSS | Plant Influent | 1200 |  | mg/L | TSS-PI-01 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | TSS (mg/L)
1 | 2020-06-29 | 9:40 | TSS | Primary Effluent | 64 |  | mg/L | TSS-PE-01 | NYEnvironmental | samples from trough No.2 (4th from the ending) Not typical of Primary Effluent | x |  |  | Potential Outlier | TSS (mg/L)
1 | 2020-06-29 | 8:50 | TSS | Final Tank Effluent | 7.3 |  | mg/L | TSS-FTE-01 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | TSS (mg/L)
1 | 2020-06-29 | 8:00 | TSS | CCT Effluent | 6 |  | mg/L | TSS-CCTE-01 | NYEnvironmental | from small access hole at North end of the CCT's |  |  |  |  | TSS (mg/L)
1 | 2020-06-29 | 8:00 | pH | CCT Effluent | 7.07 |  | - | pH-CCTE-01 | MDE | from small access hole at North end of the CCT's Not typical of CCT Effluent |  |  |  | Potential Outlier | pH (-)
1 | 2020-06-29 | 8:00 | Temperature | CCT Effluent | 28.4 |  | C | T-CCTE-01 | MDE | from small access hole at North end of the CCT's |  |  |  |  | Temperature (C)
1 | 2020-06-29 | 8:00 | Field TRC | CCT Effluent | 0.38 |  | mg/L | FTRC-CCTE-01 | MDE | from small access hole at North end of the CCT's |  |  |  |  | Field TRC (mg/L)
2 | 2020-06-30 | 9:55 | cBOD | Plant Influent | 1400 |  | mg/L | cBOD-PI-02 | NYEnvironmental | Samples from screen No.1(First from exit door)Not typical of Plant Influent | x |  |  | Potential Outlier | cBOD (mg/L)
2 | 2020-06-30 | 9:15 | cBOD | Primary Effluent | 180 |  | mg/L | cBOD-PE-02 | NYEnvironmental | [5 empty] | cBOD (mg/L)
2 | 2020-06-30 | 8:25 | cBOD | Final Tank Effluent | 7.7 |  | mg/L | cBOD-FTE-02 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | cBOD (mg/L)
2 | 2020-06-30 | 7:45 | cBOD | CCT Effluent | 12 |  | mg/L | cBOD-CCTE-02 | NYEnvironmental | from small access hole at North end of the CCT's |  |  |  |  | cBOD (mg/L)
2 | 2020-06-30 | 9:55 | pH | Plant Influent | 6.97 | 7.36 | - | pH-PI-02 | MDE | Samples from screen No.1(First from exit door) Outside of QA/QC limits |  |  | 5.443% | Potential Outlier | pH (-)
2 | 2020-06-30 | 9:55 | Temperature | Plant Influent | 28 | 27.1 | C | T-PI-02 | MDE | Samples from screen No.1(First from exit door) |  |  | 3.267% |  | Temperature (C)
2 | 2020-06-30 | 9:55 | Field TRC | Plant Influent | 2.04 |  | mg/L | FTRC-PI-02 | MDE | Samples from screen No.1(First from exit door) |  |  |  |  | Field TRC (mg/L)
2 | 2020-06-30 | 9:55 | Enterococcus | Plant Influent | 268200 |  | MPN/100mL | EC-PI-02 | NYEnvironmental | Samples from screen No.1(First from exit door) Not typical of Plant Influent |  |  |  | Potential Outlier | Enterococcus (MPN/100mL)
2 | 2020-06-30 | 9:15 | Enterococcus | Primary Effluent | 633000 |  | MPN/100mL | EC-PE-02 | NYEnvironmental | samples from trough No.2 (3rd from the ending) |  |  |  |  | Enterococcus (MPN/100mL)
2 | 2020-06-30 | 8:25 | Enterococcus | Final Tank Effluent | 17500 |  | MPN/100mL | EC-FTE-02 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
2 | 2020-06-30 | 8:25 | Enterococcus | CCT Effluent | 195 |  | MPN/100mL | EC-CCTE-02 | NYEnvironmental | from small access hole at North end of the CCT's |  |  |  |  | Enterococcus (MPN/100mL)
2 | 2020-06-30 | 9:15 | pH | Primary Effluent | 7.07 | 7.33 | - | pH-PE-02 | MDE | samples from trough No.2 (3rd from the ending) |  |  | 3.611% |  | pH (-)
2 | 2020-06-30 | 9:15 | Temperature | Primary Effluent | 25 | 24.8 | C | T-PE-02 | MDE | samples from trough No.2 (3rd from the ending) |  |  | 0.8032% |  | Temperature (C)
2 | 2020-06-30 | 9:15 | Field TRC | Primary Effluent | 0.01 |  | mg/L | FTRC-PE-02 | MDE | samples from trough No.2 (3rd from the ending) |  |  |  |  | Field TRC (mg/L)
2 | 2020-06-30 | 7:45 | Enterococcus | Final Tank Effluent | 19650 |  | MPN/100mL | EC-FTE-02 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
2 | 2020-06-30 | 9:55 | Fecal Coliform | Plant Influent | 7070000 |  | MPN/100mL | FC-PI-02 | NYEnvironmental | Samples from screen No.1(First from exit door) |  |  |  |  | Fecal Coliform (MPN/100mL)
2 | 2020-06-30 | 9:15 | Fecal Coliform | Primary Effluent | 3070000 |  | MPN/100mL | FC-PE-02 | NYEnvironmental | samples from trough No.2 (3rd from the ending) |  |  |  |  | Fecal Coliform (MPN/100mL)
2 | 2020-06-30 | 8:25 | Fecal Coliform | Final Tank Effluent | 1380000 |  | MPN/100mL | FC-FTE-02 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | Fecal Coliform (MPN/100mL)
2 | 2020-06-30 | 8:25 | pH | Final Tank Effluent | 7.54 | 7.88 | - | pH-FTE-02 | MDE | samples from last channels/final tank |  |  | 4.41% |  | pH (-)
2 | 2020-06-30 | 8:25 | Temperature | Final Tank Effluent | 25 | 24.7 | C | T-FTE-02 | MDE | samples from last channels/final tank |  |  | 1.207% |  | Temperature (C)
2 | 2020-06-30 | 8:25 | Field TRC | Final Tank Effluent | 0.08 |  | mg/L | FTRC-FTE-02 | MDE | samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
2 | 2020-06-30 | 8:25 | Fecal Coliform | CCT Effluent | 3850 |  | MPN/100mL | FC-CCTE-02 | NYEnvironmental | from small access hole at North end of the CCT's Not typical of CCT Effluent |  |  |  | Potential Outlier | Fecal Coliform (MPN/100mL)
2 | 2020-06-30 | 8:25 | Fecal Coliform | Final Tank Effluent | 1300000 |  | MPN/100mL | FC-FTE-02 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | Fecal Coliform (MPN/100mL)
2 | 2020-06-30 | 9:55 | TSS | Plant Influent | 3500 |  | mg/L | TSS-PI-02 | NYEnvironmental | Samples from screen No.1(First from exit door) Not typical of Plant Influent | x |  |  | Potential Outlier | TSS (mg/L)
2 | 2020-06-30 | 9:15 | TSS | Primary Effluent | 60 |  | mg/L | TSS-PE-02 | NYEnvironmental | samples from trough No.2 (3rd from the ending) |  |  |  |  | TSS (mg/L)
2 | 2020-06-30 | 7:45 | pH | CCT Effluent | 7.46 | 7.7 | - | pH-CCTE-02 | MDE | from small access hole at North end of the CCT's |  |  | 3.166% |  | pH (-)
2 | 2020-06-30 | 7:45 | Temperature | CCT Effluent | 24.4 | 24.4 | C | T-CCTE-02 | MDE | from small access hole at North end of the CCT's |  |  | 0% |  | Temperature (C)
2 | 2020-06-30 | 7:45 | Field TRC | CCT Effluent | 0.06 |  | mg/L | FTRC-CCTE-02 | MDE | from small access hole at North end of the CCT's |  |  |  |  | Field TRC (mg/L)
2 | 2020-06-30 | 8:25 | TSS | Final Tank Effluent | 6.7 |  | mg/L | TSS-FTE-02 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | TSS (mg/L)
2 | 2020-06-30 | 7:45 | TSS | CCT Effluent | 8 |  | mg/L | TSS-CCTE-02 | NYEnvironmental | from small access hole at North end of the CCT's |  |  |  |  | TSS (mg/L)
3 | 2020-07-01 | 9:33 | cBOD | Plant Influent | 1700 |  | mg/L | cBOD-PI-03 | NYEnvironmental | Samples from screen No.2(the middle) Not typical of cBOD Plant influent | x |  |  | Potential Outlier | cBOD (mg/L)
3 | 2020-07-01 | 8:49 | cBOD | Primary Effluent | 180 |  | mg/L | cBOD-PE-03 | NYEnvironmental | samples from trough No.2 (2nd from the ending |  |  |  |  | cBOD (mg/L)
3 | 2020-07-01 | 9:33 | pH | Plant Influent | 7.05 | 7.38 | - | pH-PI-03 | MDE | Samples from screen No.2(the middle) Outside of QA/QC limits |  |  | 4.574% | Potential Outlier | pH (-)
3 | 2020-07-01 | 9:33 | Temperature | Plant Influent | 26.9 | 26.3 | C | T-PI-03 | MDE | Samples from screen No.2(the middle) |  |  | 2.256% |  | Temperature (C)
3 | 2020-07-01 | 9:33 | Field TRC | Plant Influent | 0.21 |  | mg/L | FTRC-PI-03 | MDE | Samples from screen No.2(the middle) |  |  |  |  | Field TRC (mg/L)
3 | 2020-07-01 | 8:09 | cBOD | Final Tank Effluent | 4 |  | mg/L | cBOD-FTE-03 | NYEnvironmental | samples from last channels/final tank |  | < |  |  | cBOD (mg/L)
3 | 2020-07-01 | 7:34 | cBOD | CCT Effluent | 4 |  | mg/L | cBOD-CCTE-03 | NYEnvironmental | from small access hole at North end of the CCT's |  | < |  |  | cBOD (mg/L)
3 | 2020-07-01 | 9:33 | Enterococcus | Plant Influent | 1093500 |  | MPN/100mL | EC-PI-03 | NYEnvironmental | Samples from screen No.2(the middle) |  |  |  |  | Enterococcus (MPN/100mL)
3 | 2020-07-01 | 8:49 | Enterococcus | Primary Effluent | 589000 |  | MPN/100mL | EC-PE-03 | NYEnvironmental | samples from trough No.2 (2nd from the ending |  |  |  |  | Enterococcus (MPN/100mL)
3 | 2020-07-01 | 8:49 | pH | Primary Effluent | 7.2 | 7.46 | - | pH-PE-03 | MDE | samples from trough No.2 (2nd from the ending) |  |  | 3.547% |  | pH (-)
3 | 2020-07-01 | 8:49 | Temperature | Primary Effluent | 24.5 | 24.1 | C | T-PE-03 | MDE | samples from trough No.2 (2nd from the ending |  |  | 1.646% |  | Temperature (C)
3 | 2020-07-01 | 8:49 | Field TRC | Primary Effluent | 0.11 |  | mg/L | FTRC-PE-03 | MDE | samples from trough No.2 (2nd from the ending |  |  |  |  | Field TRC (mg/L)
3 | 2020-07-01 | 8:09 | Enterococcus | Final Tank Effluent | 37700 |  | MPN/100mL | EC-FTE-03 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
3 | 2020-07-01 | 7:34 | Enterococcus | CCT Effluent | 188.5 |  | MPN/100mL | EC-CCTE-03 | NYEnvironmental | from small access hole at North end of the CCT's |  |  |  |  | Enterococcus (MPN/100mL)
3 | 2020-07-01 | 8:09 | Enterococcus | Final Tank Effluent | 62300 |  | MPN/100mL | EC-FTE-03 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
3 | 2020-07-01 | 9:33 | Fecal Coliform | Plant Influent | 5600000 |  | MPN/100mL | FC-PI-03 | NYEnvironmental | Samples from screen No.2(the middle) |  |  |  |  | Fecal Coliform (MPN/100mL)
3 | 2020-07-01 | 8:09 | pH | Final Tank Effluent | 7.41 | 7.8 | - | pH-FTE-03 | MDE | samples from last channels/final tank |  |  | 5.128% |  | pH (-)
3 | 2020-07-01 | 8:09 | Temperature | Final Tank Effluent | 24.6 | 24.7 | C | T-FTE-03 | MDE | samples from last channels/final tank |  |  | 0.4057% |  | Temperature (C)
3 | 2020-07-01 | 8:09 | Field TRC | Final Tank Effluent | 0.04 |  | mg/L | FTRC-FTE-03 | MDE | samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
3 | 2020-07-01 | 8:49 | Fecal Coliform | Primary Effluent | 4040000 |  | MPN/100mL | FC-PE-03 | NYEnvironmental | samples from trough No.2 (2nd from the ending |  |  |  |  | Fecal Coliform (MPN/100mL)
3 | 2020-07-01 | 8:09 | Fecal Coliform | Final Tank Effluent | 287000 |  | MPN/100mL | FC-FTE-03 | NYEnvironmental | samples from last channels/final tank Not typical of Final Tank Effluent |  |  |  | Potential Outlier | Fecal Coliform (MPN/100mL)
3 | 2020-07-01 | 7:34 | Fecal Coliform | CCT Effluent | 117 |  | MPN/100mL | FC-CCTE-03 | NYEnvironmental | from small access hole at North end of the CCT's |  |  |  |  | Fecal Coliform (MPN/100mL)
3 | 2020-07-01 | 8:09 | Fecal Coliform | Final Tank Effluent | 5230000 |  | MPN/100mL | FC-FTE-03 | NYEnvironmental | samples from last channels/final tank Not typical of Final Tank Effluent |  |  |  | Potential Outlier | Fecal Coliform (MPN/100mL)
3 | 2020-07-01 | 7:34 | pH | CCT Effluent | 7.41 | 7.75 | - | pH-CCTE-03 | MDE | from small access hole at North end of the CCT's |  |  | 4.485% |  | pH (-)
3 | 2020-07-01 | 7:34 | Temperature | CCT Effluent | 23.5 | 23.7 | C | T-CCTE-03 | MDE | from small access hole at North end of the CCT's |  |  | 0.8475% |  | Temperature (C)
3 | 2020-07-01 | 7:34 | Field TRC | CCT Effluent | 0.38 |  | mg/L | FTRC-CCTE-03 | MDE | from small access hole at North end of the CCT's |  |  |  |  | Field TRC (mg/L)
3 | 2020-07-01 | 9:33 | TSS | Plant Influent | 3700 |  | mg/L | TSS-PI-03 | NYEnvironmental | Samples from screen No.2(the middle) Not typical of Plant Influent TSS | x |  |  | Potential Outlier | TSS (mg/L)
3 | 2020-07-01 | 8:49 | TSS | Primary Effluent | 66 |  | mg/L | TSS-PE-03 | NYEnvironmental | samples from trough No.2 (2nd from the ending |  |  |  |  | TSS (mg/L)
3 | 2020-07-01 | 8:09 | TSS | Final Tank Effluent | 10 |  | mg/L | TSS-FTE-03 | NYEnvironmental | samples from last channels/final tank |  |  |  |  | TSS (mg/L)
3 | 2020-07-01 | 7:34 | TSS | CCT Effluent | 8 |  | mg/L | TSS-CCTE-03 | NYEnvironmental | from small access hole at North end of the CCT's |  |  |  |  | TSS (mg/L)
4 | 2020-07-07 | 9:30 | pH | Plant Influent | 7.33 | 7.66 | - | pH-PI-04 | MDE | Samples from screen No.2(the middle) |  |  | 4.403% |  | pH (-)
4 | 2020-07-07 | 9:30 | Temperature | Plant Influent | 27.7 | 26.2 | C | T-PI-04 | MDE | Samples from screen No.2(the middle) |  |  | 5.566% |  | Temperature (C)
4 | 2020-07-07 | 9:30 | Field TRC | Plant Influent | 0.19 |  | mg/L | FTRC-PI-04 | MDE | Samples from screen No.2(the middle) |  |  |  |  | Field TRC (mg/L)
4 | 2020-07-07 | 9:30 | cBOD | Plant Influent | 170 |  | mg/L | cBOD-PI-04 | NYEnvironmental | Samples from screen No.2(the middle) |  |  |  |  | cBOD (mg/L)
4 | 2020-07-07 | 8:59 | cBOD | Primary Effluent | 67 |  | mg/L | cBOD-PE-04 | NYEnvironmental | samples from trough No.2 (3rd from the ending) |  |  |  |  | cBOD (mg/L)
4 | 2020-07-07 | 8:15 | cBOD | Final Tank Effluent | 5 |  | mg/L | cBOD-FTE-04 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | cBOD (mg/L)
4 | 2020-07-07 | 7:40 | cBOD | CCT Effluent | 4.7 |  | mg/L | cBOD-CCTE-04 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | cBOD (mg/L)
4 | 2020-07-07 | 8:59 | pH | Primary Effluent | 7.35 | 7.71 | - | pH-PE-04 | MDE | samples from trough No.2 (3rd from the ending) |  |  | 4.781% |  | pH (-)
4 | 2020-07-07 | 8:59 | Temperature | Primary Effluent | 25.9 | 24.8 | C | T-PE-04 | MDE | samples from trough No.2 (3rd from the ending) |  |  | 4.339% |  | Temperature (C)
4 | 2020-07-07 | 8:59 | Field TRC | Primary Effluent | 0.07 |  | mg/L | FTRC-PE-04 | MDE | samples from trough No.2 (3rd from the ending) |  |  |  |  | Field TRC (mg/L)
4 | 2020-07-07 | 9:30 | Enterococcus | Plant Influent | 1023000 |  | MPN/100mL | EC-PI-04 | NYEnvironmental | Samples from screen No.2(the middle) |  |  |  |  | Enterococcus (MPN/100mL)
4 | 2020-07-07 | 8:59 | Enterococcus | Primary Effluent | 698000 |  | MPN/100mL | EC-PE-04 | NYEnvironmental | samples from trough No.2 (3rd from the ending) |  |  |  |  | Enterococcus (MPN/100mL)
4 | 2020-07-07 | 8:15 | Enterococcus | Final Tank Effluent | 55600 |  | MPN/100mL | EC-FTE-04 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
4 | 2020-07-07 | 7:40 | Enterococcus | CCT Effluent | 232.5 |  | MPN/100mL | EC-CCTE-04 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | Enterococcus (MPN/100mL)
4 | 2020-07-07 | 8:15 | pH | Final Tank Effluent | 7.31 | 7.73 | - | pH-FTE-04 | MDE | Samples from last channels/final tank |  |  | 5.585% |  | pH (-)
4 | 2020-07-07 | 8:15 | Temperature | Final Tank Effluent | 26 | 25.2 | C | T-FTE-04 | MDE | Samples from last channels/final tank |  |  | 3.125% |  | Temperature (C)
4 | 2020-07-07 | 8:15 | Field TRC | Final Tank Effluent | 0.09 |  | mg/L | FTRC-FTE-04 | MDE | Samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
4 | 2020-07-07 | 8:15 | Enterococcus | Final Tank Effluent | 57250 |  | MPN/100mL | EC-FTE-04 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
4 | 2020-07-07 | 9:30 | Fecal Coliform | Plant Influent |  |  | MPN/100mL | FC-PI-04 | NYEnvironmental | VOID Samples from screen No.2(the middle) Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
4 | 2020-07-07 | 8:59 | Fecal Coliform | Primary Effluent |  |  | MPN/100mL | FC-PE-04 | NYEnvironmental | VOID samples from trough No.2 (3rd from the ending) Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
4 | 2020-07-07 | 8:15 | Fecal Coliform | Final Tank Effluent |  |  | MPN/100mL | FC-FTE-04 | NYEnvironmental | VOID Samples from last channels/final tank. Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
4 | 2020-07-07 | 7:40 | pH | CCT Effluent | 7.44 | 8.12 | - | pH-CCTE-04 | MDE | From small access hole at North end of the CCT's. Issue with water bath having drifted in its setpoint, resulting in poor growth |  |  | 8.74% |  | pH (-)
4 | 2020-07-07 | 7:40 | Temperature | CCT Effluent | 25.3 | 24.5 | C | T-CCTE-04 | MDE | From small access hole at North end of the CCT's. Issue with water bath having drifted in its setpoint, resulting in poor growth |  |  | 3.213% |  | Temperature (C)
4 | 2020-07-07 | 7:40 | Field TRC | CCT Effluent | 0.29 |  | mg/L | FTRC-CCTE-04 | MDE | From small access hole at North end of the CCT's. Issue with water bath having drifted in its setpoint, resulting in poor growth |  |  |  |  | Field TRC (mg/L)
4 | 2020-07-07 | 7:40 | Fecal Coliform | CCT Effluent |  |  | MPN/100mL | FC-CCTE-04 | NYEnvironmental | VOID From small access hole at North end of the CCT's. Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
4 | 2020-07-07 | 8:15 | Fecal Coliform | Final Tank Effluent |  |  | MPN/100mL | FC-FTE-04 | NYEnvironmental | VOID Samples from last channels/final tank. Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
4 | 2020-07-07 | 9:30 | TSS | Plant Influent | 120 |  | mg/L | TSS-PI-04 | NYEnvironmental | Samples from screen No.2(the middle) |  |  |  |  | TSS (mg/L)
4 | 2020-07-07 | 8:59 | TSS | Primary Effluent | 58 |  | mg/L | TSS-PE-04 | NYEnvironmental | samples from trough No.2 (3rd from the ending) |  |  |  |  | TSS (mg/L)
4 | 2020-07-07 | 8:15 | TSS | Final Tank Effluent | 11 |  | mg/L | TSS-FTE-04 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | TSS (mg/L)
4 | 2020-07-07 | 7:40 | TSS | CCT Effluent | 12 |  | mg/L | TSS-CCTE-04 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | TSS (mg/L)
5 | 2020-07-08 | 9:26 | pH | Plant Influent | 7.35 | 7.67 | - | pH-PI-05 | MDE | Samples from screen No.3(last from exit door) |  |  | 4.261% |  | pH (-)
5 | 2020-07-08 | 9:26 | Temperature | Plant Influent | 27.6 | 27.2 | C | T-PI-05 | MDE | Samples from screen No.3(last from exit door) |  |  | 1.46% |  | Temperature (C)
5 | 2020-07-08 | 9:26 | Field TRC | Plant Influent | 0.21 |  | mg/L | FTRC-PI-05 | MDE | Samples from screen No.3(last from exit door) |  |  |  |  | Field TRC (mg/L)
5 | 2020-07-08 | 9:26 | cBOD | Plant Influent | 110 |  | mg/L | cBOD-PI-05 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | cBOD (mg/L)
5 | 2020-07-08 | 8:45 | cBOD | Primary Effluent | 73 |  | mg/L | cBOD-PE-05 | NYEnvironmental | Samples from trough No.2 (2nd from the ending |  |  |  |  | cBOD (mg/L)
5 | 2020-07-08 | 8:45 | pH | Primary Effluent | 7.21 | 7.53 | - | pH-PE-05 | MDE | Samples from trough No.2 (2nd from the ending |  |  | 4.342% |  | pH (-)
5 | 2020-07-08 | 8:45 | Temperature | Primary Effluent | 26.6 | 25.7 | C | T-PE-05 | MDE | Samples from trough No.2 (2nd from the ending |  |  | 3.442% |  | Temperature (C)
5 | 2020-07-08 | 8:45 | Field TRC | Primary Effluent | 0.02 |  | mg/L | FTRC-PE-05 | MDE | Samples from trough No.2 (2nd from the ending |  |  |  |  | Field TRC (mg/L)
5 | 2020-07-08 | 8:12 | cBOD | Final Tank Effluent | 4 |  | mg/L | cBOD-FTE-05 | NYEnvironmental | Samples from last channels/final tank |  | < |  |  | cBOD (mg/L)
5 | 2020-07-08 | 7:39 | cBOD | CCT Effluent | 4 |  | mg/L | cBOD-CCTE-05 | NYEnvironmental | From small access hole at North end of the CCT's |  | < |  |  | cBOD (mg/L)
5 | 2020-07-08 | 9:26 | Enterococcus | Plant Influent | 920800 |  | MPN/100mL | EC-PI-05 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | Enterococcus (MPN/100mL)
5 | 2020-07-08 | 8:45 | Enterococcus | Primary Effluent | 517200 |  | MPN/100mL | EC-PE-05 | NYEnvironmental | Samples from trough No.2 (2nd from the ending |  |  |  |  | Enterococcus (MPN/100mL)
5 | 2020-07-08 | 8:12 | pH | Final Tank Effluent | 7.48 | 7.88 | - | pH-FTE-05 | MDE | Samples from last channels/final tank |  |  | 5.208% |  | pH (-)
5 | 2020-07-08 | 8:12 | Temperature | Final Tank Effluent | 26.8 | 26.2 | C | T-FTE-05 | MDE | Samples from last channels/final tank |  |  | 2.264% |  | Temperature (C)
5 | 2020-07-08 | 8:12 | Field TRC | Final Tank Effluent | 0.02 |  | mg/L | FTRC-FTE-05 | MDE | Samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
5 | 2020-07-08 | 8:12 | Enterococcus | Final Tank Effluent | 162750 |  | MPN/100mL | EC-FTE-05 | NYEnvironmental | samples from last channels/final tank Not typical of Final Tank Effluent |  |  |  | Potential Outlier | Enterococcus (MPN/100mL)
5 | 2020-07-08 | 7:39 | Enterococcus | CCT Effluent | 49 |  | MPN/100mL | EC-CCTE-05 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | Enterococcus (MPN/100mL)
5 | 2020-07-08 | 8:12 | Enterococcus | Final Tank Effluent | 52300 |  | MPN/100mL | EC-FTE-05 | NYEnvironmental | samples from last channels/final tank Not typical of Final Tank Effluent |  |  |  | Potential Outlier | Enterococcus (MPN/100mL)
5 | 2020-07-08 | 9:26 | Fecal Coliform | Plant Influent |  |  | MPN/100mL | FC-PI-05 | NYEnvironmental | VOID Samples from screen No.3(last from exit door). Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
5 | 2020-07-08 | 7:39 | pH | CCT Effluent | 7.49 | 8.02 | - | pH-CCTE-05 | MDE | From small access hole at North end of the CCT's |  |  | 6.834% |  | pH (-)
5 | 2020-07-08 | 7:39 | Temperature | CCT Effluent | 27 | 26.1 | C | T-CCTE-05 | MDE | From small access hole at North end of the CCT's |  |  | 3.39% |  | Temperature (C)
5 | 2020-07-08 | 7:39 | Field TRC | CCT Effluent | 0.47 |  | mg/L | FTRC-CCTE-05 | MDE | From small access hole at North end of the CCT's |  |  |  |  | Field TRC (mg/L)
5 | 2020-07-08 | 8:45 | Fecal Coliform | Primary Effluent |  |  | MPN/100mL | FC-PE-05 | NYEnvironmental | VOID Samples from trough No.2 (2nd from the ending). Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
5 | 2020-07-08 | 8:12 | Fecal Coliform | Final Tank Effluent |  |  | MPN/100mL | FC-FTE-05 | NYEnvironmental | VOID Samples from last channels/final tank. Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
5 | 2020-07-08 | 7:39 | Fecal Coliform | CCT Effluent |  |  | MPN/100mL | FC-CCTE-05 | NYEnvironmental | VOID From small access hole at North end of the CCT's. Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
5 | 2020-07-08 | 8:12 | Fecal Coliform | Final Tank Effluent |  |  | MPN/100mL | FC-FTE-05 | NYEnvironmental | VOID Samples from last channels/final tank. Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
5 | 2020-07-08 | 9:26 | TSS | Plant Influent | 120 |  | mg/L | TSS-PI-05 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | TSS (mg/L)
5 | 2020-07-08 | 8:45 | TSS | Primary Effluent | 57 |  | mg/L | TSS-PE-05 | NYEnvironmental | Samples from trough No.2 (2nd from the ending |  |  |  |  | TSS (mg/L)
5 | 2020-07-08 | 8:12 | TSS | Final Tank Effluent | 8 |  | mg/L | TSS-FTE-05 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | TSS (mg/L)
5 | 2020-07-08 | 7:39 | TSS | CCT Effluent | 6 |  | mg/L | TSS-CCTE-05 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | TSS (mg/L)
6 | 2020-07-09 | 9:19 | pH | Plant Influent | 7.38 | 7.76 | - | pH-PI-06 | MDE | Samples from screen No.1(First from exit door) |  |  | 5.02% |  | pH (-)
6 | 2020-07-09 | 9:19 | Temperature | Plant Influent | 27.6 | 26.8 | C | T-PI-06 | MDE | Samples from screen No.1(First from exit door) |  |  | 2.941% |  | Temperature (C)
6 | 2020-07-09 | 9:19 | Field TRC | Plant Influent | 0.19 |  | mg/L | FTRC-PI-06 | MDE | Samples from screen No.1(First from exit door) |  |  |  |  | Field TRC (mg/L)
6 | 2020-07-09 | 8:43 | pH | Primary Effluent | 7.37 | 7.68 | - | pH-PE-06 | MDE | Samples from trough No.2 (3rd from the ending) |  |  | 4.12% |  | pH (-)
6 | 2020-07-09 | 8:43 | Temperature | Primary Effluent | 26.1 | 25.2 | C | T-PE-06 | MDE | Samples from trough No.2 (3rd from the ending) |  |  | 3.509% |  | Temperature (C)
6 | 2020-07-09 | 8:43 | Field TRC | Primary Effluent | 0.02 |  | mg/L | FTRC-PE-06 | MDE | Samples from trough No.2 (3rd from the ending) |  |  |  |  | Field TRC (mg/L)
6 | 2020-07-09 | 9:19 | cBOD | Plant Influent | 160 |  | mg/L | cBOD-PI-06 | NYEnvironmental | Samples from screen No.1(First from exit door) |  |  |  |  | cBOD (mg/L)
6 | 2020-07-09 | 8:43 | cBOD | Primary Effluent | 98 |  | mg/L | cBOD-PE-06 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | cBOD (mg/L)
6 | 2020-07-09 | 8:15 | cBOD | Final Tank Effluent | 4.9 |  | mg/L | cBOD-FTE-06 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | cBOD (mg/L)
6 | 2020-07-09 | 7:42 | cBOD | CCT Effluent | 4 |  | mg/L | cBOD-CCTE-06 | NYEnvironmental | From small access hole at North end of the CCT's |  | < |  |  | cBOD (mg/L)
6 | 2020-07-09 | 8:15 | pH | Final Tank Effluent | 7.42 | 7.81 | - | pH-FTE-06 | MDE | Samples from last channels/final tank |  |  | 5.121% |  | pH (-)
6 | 2020-07-09 | 8:15 | Temperature | Final Tank Effluent | 26.4 | 25.5 | C | T-FTE-06 | MDE | Samples from last channels/final tank |  |  | 3.468% |  | Temperature (C)
6 | 2020-07-09 | 8:15 | Field TRC | Final Tank Effluent | 0.22 |  | mg/L | FTRC-FTE-06 | MDE | Samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
6 | 2020-07-09 | 9:19 | Enterococcus | Plant Influent | 1093500 |  | MPN/100mL | EC-PI-06 | NYEnvironmental | Samples from screen No.1(First from exit door) |  |  |  |  | Enterococcus (MPN/100mL)
6 | 2020-07-09 | 8:43 | Enterococcus | Primary Effluent | 930000 |  | MPN/100mL | EC-PE-06 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | Enterococcus (MPN/100mL)
6 | 2020-07-09 | 8:15 | Enterococcus | Final Tank Effluent | 29700 |  | MPN/100mL | EC-FTE-06 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
6 | 2020-07-09 | 7:42 | Enterococcus | CCT Effluent | 49 |  | MPN/100mL | EC-CCTE-06 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | Enterococcus (MPN/100mL)
6 | 2020-07-09 | 7:42 | pH | CCT Effluent | 7.5 | 8.08 | - | pH-CCTE-06 | MDE | From small access hole at North end of the CCT's |  |  | 7.445% |  | pH (-)
6 | 2020-07-09 | 7:42 | Temperature | CCT Effluent | 26.9 | 26.4 | C | T-CCTE-06 | MDE | From small access hole at North end of the CCT's |  |  | 1.876% |  | Temperature (C)
6 | 2020-07-09 | 7:42 | Field TRC | CCT Effluent | 0.33 |  | mg/L | FTRC-CCTE-06 | MDE | From small access hole at North end of the CCT's |  |  |  |  | Field TRC (mg/L)
6 | 2020-07-09 | 8:15 | Enterococcus | Final Tank Effluent | 39700 |  | MPN/100mL | EC-FTE-06 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
6 | 2020-07-09 | 9:19 | Fecal Coliform | Plant Influent |  |  | MPN/100mL | FC-PI-06 | NYEnvironmental | VOID Samples from screen No.1(First from exit door). Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
6 | 2020-07-09 | 8:43 | Fecal Coliform | Primary Effluent |  |  | MPN/100mL | FC-PE-06 | NYEnvironmental | VOID Samples from trough No.2 (3rd from the ending). Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
6 | 2020-07-09 | 8:15 | Fecal Coliform | Final Tank Effluent |  |  | MPN/100mL | FC-FTE-06 | NYEnvironmental | VOID Samples from last channels/final tank. Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
6 | 2020-07-09 | 7:42 | Fecal Coliform | CCT Effluent |  |  | MPN/100mL | FC-CCTE-06 | NYEnvironmental | VOID From small access hole at North end of the CCT's. Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
6 | 2020-07-09 | 8:15 | Fecal Coliform | Final Tank Effluent |  |  | MPN/100mL | FC-FTE-06 | NYEnvironmental | VOID Samples from last channels/final tank. Issue with water bath having drifted in its setpoint, resulting in poor growth | X |  |  |  | Fecal Coliform (MPN/100mL)
6 | 2020-07-09 | 9:19 | TSS | Plant Influent | 98 |  | mg/L | TSS-PI-06 | NYEnvironmental | Samples from screen No.1(First from exit door) |  |  |  |  | TSS (mg/L)
6 | 2020-07-09 | 8:43 | TSS | Primary Effluent | 45 |  | mg/L | TSS-PE-06 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | TSS (mg/L)
6 | 2020-07-09 | 8:15 | TSS | Final Tank Effluent | 4 |  | mg/L | TSS-FTE-06 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | TSS (mg/L)
6 | 2020-07-09 | 7:42 | TSS | CCT Effluent | 4 |  | mg/L | TSS-CCTE-06 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | TSS (mg/L)
6 | 2020-07-09 | 10:20 | Particle Size Distribution XAD | Aeration Tank Effluent |  |  | - | XAD-ATE-06 | Manhattan College | Sample location I.D. # PR327299 |  |  |  |  | Particle Size Distribution XAD (-)
7 | 2020-07-10 | 9:10 | pH | Plant Influent | 7.21 | 7.55 | - | pH-PI-07 | MDE | Samples from screen No.2(the middle) |  |  | 4.607% |  | pH (-)
7 | 2020-07-10 | 9:10 | Temperature | Plant Influent | 26.9 | 26.6 | C | T-PI-07 | MDE | Samples from screen No.2(the middle) |  |  | 1.121% |  | Temperature (C)
7 | 2020-07-10 | 9:10 | Field TRC | Plant Influent | 0.63 |  | mg/L | FTRC-PI-07 | MDE | Samples from screen No.2(the middle) |  |  |  |  | Field TRC (mg/L)
7 | 2020-07-10 | 8:38 | pH | Primary Effluent | 7.23 | 7.53 | - | pH-PE-07 | MDE | Samples from trough No.2 (2nd from the ending |  |  | 4.065% |  | pH (-)
7 | 2020-07-10 | 8:38 | Temperature | Primary Effluent | 26.4 | 25.9 | C | T-PE-07 | MDE | Samples from trough No.2 (2nd from the ending |  |  | 1.912% |  | Temperature (C)
7 | 2020-07-10 | 8:38 | Field TRC | Primary Effluent | 0.04 |  | mg/L | FTRC-PE-07 | MDE | Samples from trough No.2 (2nd from the ending |  |  |  |  | Field TRC (mg/L)
7 | 2020-07-10 | 9:10 | cBOD | Plant Influent |  |  | mg/L | cBOD-PI-07 | NYEnvironmental | Samples from screen No.2(the middle). Out of holding time | X |  |  |  | cBOD (mg/L)
7 | 2020-07-10 | 8:10 | pH | Final Tank Effluent | 7.41 | 7.79 | - | pH-FTE-07 | MDE | Samples from last channels/final tank. |  |  | 5% |  | pH (-)
7 | 2020-07-10 | 8:10 | Temperature | Final Tank Effluent | 26.1 | 25.8 | C | T-FTE-07 | MDE | Samples from last channels/final tank |  |  | 1.156% |  | Temperature (C)
7 | 2020-07-10 | 8:10 | Field TRC | Final Tank Effluent | 0.13 |  | mg/L | FTRC-FTE-07 | MDE | Samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
7 | 2020-07-10 | 8:38 | cBOD | Primary Effluent |  |  | mg/L | cBOD-PE-07 | NYEnvironmental | Samples from trough No.2 (2nd from the ending). Out of holding time | X |  |  |  | cBOD (mg/L)
7 | 2020-07-10 | 8:10 | cBOD | Final Tank Effluent |  |  | mg/L | cBOD-FTE-07 | NYEnvironmental | Samples from last channels/final tank. Out of holding time | X |  |  |  | cBOD (mg/L)
7 | 2020-07-10 | 7:46 | cBOD | CCT Effluent |  |  | mg/L | cBOD-CCTE-07 | NYEnvironmental | From small access hole at North end of the CCT's. Out of holding time | X |  |  |  | cBOD (mg/L)
7 | 2020-07-10 | 9:10 | Enterococcus | Plant Influent | 1244500 |  | MPN/100mL | EC-PI-07 | NYEnvironmental | Samples from screen No.2(the middle) |  |  |  |  | Enterococcus (MPN/100mL)
7 | 2020-07-10 | 7:46 | pH | CCT Effluent | 7.49 | 8.04 | - | pH-CCTE-07 | MDE | From small access hole at North end of the CCT's |  |  | 7.083% |  | pH (-)
7 | 2020-07-10 | 7:46 | Temperature | CCT Effluent | 26.5 | 26 | C | T-CCTE-07 | MDE | From small access hole at North end of the CCT's |  |  | 1.905% |  | Temperature (C)
7 | 2020-07-10 | 7:46 | Field TRC | CCT Effluent | 0.58 |  | mg/L | FTRC-CCTE-07 | MDE | From small access hole at North end of the CCT's |  |  |  |  | Field TRC (mg/L)
7 | 2020-07-10 | 8:38 | Enterococcus | Primary Effluent | 648800 |  | MPN/100mL | EC-PE-07 | NYEnvironmental | Samples from trough No.2 (2nd from the ending |  |  |  |  | Enterococcus (MPN/100mL)
7 | 2020-07-10 | 8:10 | Enterococcus | Final Tank Effluent | 6050 |  | MPN/100mL | EC-FTE-07 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
7 | 2020-07-10 | 7:46 | Enterococcus | CCT Effluent | 5 |  | MPN/100mL | EC-CCTE-07 | NYEnvironmental | From small access hole at North end of the CCT's |  | < |  |  | Enterococcus (MPN/100mL)
7 | 2020-07-10 | 8:10 | Enterococcus | Final Tank Effluent | 9250 |  | MPN/100mL | EC-FTE-07 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
7 | 2020-07-10 | 9:10 | Fecal Coliform | Plant Influent | 1450000 |  | MPN/100mL | FC-PI-07 | NYEnvironmental | Samples from screen No.2(the middle) |  |  |  |  | Fecal Coliform (MPN/100mL)
7 | 2020-07-10 | 8:38 | Fecal Coliform | Primary Effluent | 2590000 |  | MPN/100mL | FC-PE-07 | NYEnvironmental | Samples from trough No.2 (2nd from the ending |  |  |  |  | Fecal Coliform (MPN/100mL)
7 | 2020-07-10 | 8:10 | Fecal Coliform | Final Tank Effluent | 72500 |  | MPN/100mL | FC-FTE-07 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Fecal Coliform (MPN/100mL)
7 | 2020-07-10 | 7:46 | Fecal Coliform | CCT Effluent | 94.5 |  | MPN/100mL | FC-CCTE-07 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | Fecal Coliform (MPN/100mL)
7 | 2020-07-10 | 8:10 | Fecal Coliform | Final Tank Effluent | 83200 |  | MPN/100mL | FC-FTE-07 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Fecal Coliform (MPN/100mL)
7 | 2020-07-10 | 9:10 | TSS | Plant Influent |  |  | mg/L | TSS-PI-07 | NYEnvironmental | Samples from screen No.2(the middle) |  |  |  |  | TSS (mg/L)
7 | 2020-07-10 | 8:38 | TSS | Primary Effluent |  |  | mg/L | TSS-PE-07 | NYEnvironmental | Samples from trough No.2 (2nd from the ending |  |  |  |  | TSS (mg/L)
7 | 2020-07-10 | 8:10 | TSS | Final Tank Effluent |  |  | mg/L | TSS-FTE-07 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | TSS (mg/L)
7 | 2020-07-10 | 7:46 | TSS | CCT Effluent |  |  | mg/L | TSS-CCTE-07 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | TSS (mg/L)
8 | 2020-07-13 | 9:18 | pH | Plant Influent | 7.26 | 7.54 | - | pH-PI-08 | MDE | Samples from screen No.3(last from exit door) |  |  | 3.784% |  | pH (-)
8 | 2020-07-13 | 9:18 | Temperature | Plant Influent | 21.9 | 25.9 | C | T-PI-08 | MDE | Samples from screen No.3(last from exit door) |  |  | 16.74% |  | Temperature (C)
8 | 2020-07-13 | 9:18 | Field TRC | Plant Influent | 0.08 |  | mg/L | FTRC-PI-08 | MDE | Samples from screen No.3(last from exit door) |  |  |  |  | Field TRC (mg/L)
8 | 2020-07-13 | 8:48 | pH | Primary Effluent | 7.21 | 7.51 | - | pH-PE-08 | MDE | Samples from trough No.2 (3rd from the ending) |  |  | 4.076% |  | pH (-)
8 | 2020-07-13 | 8:48 | Temperature | Primary Effluent | 22.8 | 24.6 | C | T-PE-08 | MDE | Samples from trough No.2 (3rd from the ending) |  |  | 7.595% |  | Temperature (C)
8 | 2020-07-13 | 8:48 | Field TRC | Primary Effluent | 0 |  | mg/L | FTRC-PE-08 | MDE | Samples from trough No.2 (3rd from the ending) |  |  |  |  | Field TRC (mg/L)
8 | 2020-07-13 | 8:19 | pH | Final Tank Effluent | 7.43 | 7.77 | - | pH-FTE-08 | MDE | Samples from last channels/final tank |  |  | 4.474% |  | pH (-)
8 | 2020-07-13 | 8:19 | Temperature | Final Tank Effluent | 24.1 | 25 | C | T-FTE-08 | MDE | Samples from last channels/final tank |  |  | 3.666% |  | Temperature (C)
8 | 2020-07-13 | 8:19 | Field TRC | Final Tank Effluent | 0.1 |  | mg/L | FTRC-FTE-08 | MDE | Samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
8 | 2020-07-13 | 9:18 | cBOD | Plant Influent | 200 |  | mg/L | cBOD-PI-08 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | cBOD (mg/L)
8 | 2020-07-13 | 8:48 | cBOD | Primary Effluent | 250 |  | mg/L | cBOD-PE-08 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | cBOD (mg/L)
8 | 2020-07-13 | 8:19 | cBOD | Final Tank Effluent | 4 |  | mg/L | cBOD-FTE-08 | NYEnvironmental | Samples from last channels/final tank |  | < |  |  | cBOD (mg/L)
8 | 2020-07-13 | 7:45 | pH | CCT Effluent | 7.38 | 7.87 | - | pH-CCTE-08 | MDE | From small access hole at North end of the CCT's |  |  | 6.426% |  | pH (-)
8 | 2020-07-13 | 7:45 | Temperature | CCT Effluent | 23.9 | 25.5 | C | T-CCTE-08 | MDE | From small access hole at North end of the CCT's |  |  | 6.478% |  | Temperature (C)
8 | 2020-07-13 | 7:45 | Field TRC | CCT Effluent | 0.59 |  | mg/L | FTRC-CCTE-08 | MDE | From small access hole at North end of the CCT's |  |  |  |  | Field TRC (mg/L)
8 | 2020-07-13 | 7:45 | cBOD | CCT Effluent | 4 |  | mg/L | cBOD-CCTE-08 | NYEnvironmental | From small access hole at North end of the CCT's |  | < |  |  | cBOD (mg/L)
8 | 2020-07-13 | 9:18 | Enterococcus | Plant Influent | 1892000 |  | MPN/100mL | EC-PI-08 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | Enterococcus (MPN/100mL)
8 | 2020-07-13 | 8:48 | Enterococcus | Primary Effluent | 782500 |  | MPN/100mL | EC-PE-08 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | Enterococcus (MPN/100mL)
8 | 2020-07-13 | 8:19 | Enterococcus | Final Tank Effluent | 2050 |  | MPN/100mL | EC-FTE-08 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
8 | 2020-07-13 | 7:45 | Enterococcus | CCT Effluent | 5 |  | MPN/100mL | EC-CCTE-08 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | Enterococcus (MPN/100mL)
8 | 2020-07-13 | 8:19 | Enterococcus | Final Tank Effluent | 3700 |  | MPN/100mL | EC-FTE-08 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
8 | 2020-07-13 | 9:18 | Fecal Coliform | Plant Influent | 6500000 |  | MPN/100mL | FC-PI-08 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | Fecal Coliform (MPN/100mL)
8 | 2020-07-13 | 8:48 | Fecal Coliform | Primary Effluent | 4330000 |  | MPN/100mL | FC-PE-08 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | Fecal Coliform (MPN/100mL)
8 | 2020-07-13 | 8:19 | Fecal Coliform | Final Tank Effluent | 4800 |  | MPN/100mL | FC-FTE-08 | NYEnvironmental | samples from last channels/final tank Not typical of Final Tank Effluent |  |  |  | Potential Outlier | Fecal Coliform (MPN/100mL)
8 | 2020-07-13 | 7:45 | Fecal Coliform | CCT Effluent | 26 |  | MPN/100mL | FC-CCTE-08 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | Fecal Coliform (MPN/100mL)
8 | 2020-07-13 | 8:19 | Fecal Coliform | Final Tank Effluent | 15800 |  | MPN/100mL | FC-FTE-08 | NYEnvironmental | samples from last channels/final tank Not typical of Final Tank Effluent |  |  |  | Potential Outlier | Fecal Coliform (MPN/100mL)
8 | 2020-07-13 | 9:18 | TSS | Plant Influent | 110 |  | mg/L | TSS-PI-08 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | TSS (mg/L)
8 | 2020-07-13 | 8:48 | TSS | Primary Effluent | 98 |  | mg/L | TSS-PE-08 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | TSS (mg/L)
8 | 2020-07-13 | 8:19 | TSS | Final Tank Effluent | 6 |  | mg/L | TSS-FTE-08 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | TSS (mg/L)
8 | 2020-07-13 | 7:45 | TSS | CCT Effluent | 3.3 |  | mg/L | TSS-CCTE-08 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | TSS (mg/L)
8 | 2020-07-13 | 10:00 | Particle Size Distribution XAD | Aeration Tank Effluent |  |  | - | XAD-ATE-08 | Manhattan College | Sample location I.D. # PR327299 |  |  |  |  | Particle Size Distribution XAD (-)
9 | 2020-07-14 | 9:14 | pH | Plant Influent | 7.23 | 7.53 | - | pH-PI-09 | MDE | Samples from screen No.1(First from exit door) |  |  | 4.065% |  | pH (-)
9 | 2020-07-14 | 9:14 | Temperature | Plant Influent | 25.1 | 25.1 | C | T-PI-09 | MDE | Samples from screen No.1(First from exit door) |  |  | 0% |  | Temperature (C)
9 | 2020-07-14 | 9:14 | Field TRC | Plant Influent | 0.12 |  | mg/L | FTRC-PI-09 | MDE | Samples from screen No.1(First from exit door) |  |  |  |  | Field TRC (mg/L)
9 | 2020-07-14 | 8:45 | pH | Primary Effluent | 7.28 | 7.62 | - | pH-PE-09 | MDE | Samples from trough No.2 (3rd from the ending) |  |  | 4.564% |  | pH (-)
9 | 2020-07-14 | 8:45 | Temperature | Primary Effluent | 19.7 | 23.1 | C | T-PE-09 | MDE | Samples from trough No.2 (3rd from the ending) |  |  | 15.89% |  | Temperature (C)
9 | 2020-07-14 | 8:45 | Field TRC | Primary Effluent | 0 |  | mg/L | FTRC-PE-09 | MDE | Samples from trough No.2 (3rd from the ending) |  |  |  |  | Field TRC (mg/L)
9 | 2020-07-14 | 8:08 | pH | Final Tank Effluent | 7.53 | 7.88 | - | pH-FTE-09 | MDE | Samples from last channels/final tank |  |  | 4.543% |  | pH (-)
9 | 2020-07-14 | 8:08 | Temperature | Final Tank Effluent | 22.2 | 24.1 | C | T-FTE-09 | MDE | Samples from last channels/final tank |  |  | 8.207% |  | Temperature (C)
9 | 2020-07-14 | 8:08 | Field TRC | Final Tank Effluent | 0.02 |  | mg/L | FTRC-FTE-09 | MDE | Samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
9 | 2020-07-14 | 7:43 | pH | CCT Effluent | 7.64 | 8.1 | - | pH-CCTE-09 | MDE | From small access hole at North end of the CCT's |  |  | 5.845% |  | pH (-)
9 | 2020-07-14 | 7:43 | Temperature | CCT Effluent | 23.8 | 23.9 | C | T-CCTE-09 | MDE | From small access hole at North end of the CCT's |  |  | 0.4193% |  | Temperature (C)
9 | 2020-07-14 | 7:43 | Field TRC | CCT Effluent | 0.63 |  | mg/L | FTRC-CCTE-09 | MDE | From small access hole at North end of the CCT's |  |  |  |  | Field TRC (mg/L)
9 | 2020-07-14 | 9:14 | cBOD | Plant Influent | 280 |  | mg/L | cBOD-PI-09 | NYEnvironmental | Samples from screen No.1(First from exit door) |  |  |  |  | cBOD (mg/L)
9 | 2020-07-14 | 8:45 | cBOD | Primary Effluent | 88 |  | mg/L | cBOD-PE-09 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | cBOD (mg/L)
9 | 2020-07-14 | 8:08 | cBOD | Final Tank Effluent | 4 |  | mg/L | cBOD-FTE-09 | NYEnvironmental | Samples from last channels/final tank |  | < |  |  | cBOD (mg/L)
9 | 2020-07-14 | 7:43 | cBOD | CCT Effluent | 4 |  | mg/L | cBOD-CCTE-09 | NYEnvironmental | From small access hole at North end of the CCT's |  | < |  |  | cBOD (mg/L)
9 | 2020-07-14 | 9:14 | Enterococcus | Plant Influent | 1377500 |  | MPN/100mL | EC-PI-09 | NYEnvironmental | Samples from screen No.1(First from exit door) |  |  |  |  | Enterococcus (MPN/100mL)
9 | 2020-07-14 | 8:45 | Enterococcus | Primary Effluent | 550000 |  | MPN/100mL | EC-PE-09 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | Enterococcus (MPN/100mL)
9 | 2020-07-14 | 8:08 | Enterococcus | Final Tank Effluent | 10650 |  | MPN/100mL | EC-FTE-09 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
9 | 2020-07-14 | 7:43 | Enterococcus | CCT Effluent | 5 |  | MPN/100mL | EC-CCTE-09 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | Enterococcus (MPN/100mL)
9 | 2020-07-14 | 8:08 | Enterococcus | Final Tank Effluent | 8050 |  | MPN/100mL | EC-FTE-09 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
9 | 2020-07-14 | 9:14 | Fecal Coliform | Plant Influent |  |  | MPN/100mL | FC-PI-09 | NYEnvironmental | VOID Samples from screen No.1(First from exit door) | X |  |  |  | Fecal Coliform (MPN/100mL)
9 | 2020-07-14 | 8:45 | Fecal Coliform | Primary Effluent |  |  | MPN/100mL | FC-PE-09 | NYEnvironmental | VOID Samples from trough No.2 (3rd from the ending) | X |  |  |  | Fecal Coliform (MPN/100mL)
9 | 2020-07-14 | 8:08 | Fecal Coliform | Final Tank Effluent |  |  | MPN/100mL | FC-FTE-09 | NYEnvironmental | VOID Samples from last channels/final tank | X |  |  |  | Fecal Coliform (MPN/100mL)
9 | 2020-07-14 | 7:43 | Fecal Coliform | CCT Effluent |  |  | MPN/100mL | FC-CCTE-09 | NYEnvironmental | VOID From small access hole at North end of the CCT's | X |  |  |  | Fecal Coliform (MPN/100mL)
9 | 2020-07-14 | 8:08 | Fecal Coliform | Final Tank Effluent |  |  | MPN/100mL | FC-FTE-09 | NYEnvironmental | VOID Samples from last channels/final tank | X |  |  |  | Fecal Coliform (MPN/100mL)
9 | 2020-07-14 | 9:14 | TSS | Plant Influent | 43 |  | mg/L | TSS-PI-09 | NYEnvironmental | Samples from screen No.1(First from exit door) |  |  |  |  | TSS (mg/L)
9 | 2020-07-14 | 8:45 | TSS | Primary Effluent | 120 |  | mg/L | TSS-PE-09 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | TSS (mg/L)
9 | 2020-07-14 | 8:08 | TSS | Final Tank Effluent | 5.3 |  | mg/L | TSS-FTE-09 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | TSS (mg/L)
9 | 2020-07-14 | 7:43 | TSS | CCT Effluent | 4.7 |  | mg/L | TSS-CCTE-09 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | TSS (mg/L)
10 | 2020-07-15 | 9:05 | pH | Plant Influent | 7.33 | 7.66 | - | pH-PI-10 | MDE | Samples from screen No.2(the middle) |  |  | 4.403% |  | pH (-)
10 | 2020-07-15 | 9:05 | Temperature | Plant Influent | 23.3 | 25.5 | C | T-PI-10 | MDE | Samples from screen No.2(the middle) |  |  | 9.016% |  | Temperature (C)
10 | 2020-07-15 | 9:05 | Field TRC | Plant Influent | 0.15 |  | mg/L | FTRC-PI-10 | MDE | Samples from screen No.2(the middle) |  |  |  |  | Field TRC (mg/L)
10 | 2020-07-15 | 8:40 | pH | Primary Effluent | 7.29 | 7.61 | - | pH-PE-10 | MDE | Samples from trough No.2 (2nd from the ending |  |  | 4.295% |  | pH (-)
10 | 2020-07-15 | 8:40 | Temperature | Primary Effluent | 22.9 | 23.4 | C | T-PE-10 | MDE | Samples from trough No.2 (2nd from the ending |  |  | 2.16% |  | Temperature (C)
10 | 2020-07-15 | 8:40 | Field TRC | Primary Effluent | 0.02 |  | mg/L | FTRC-PE-10 | MDE | Samples from trough No.2 (2nd from the ending |  |  |  |  | Field TRC (mg/L)
10 | 2020-07-15 | 8:10 | pH | Final Tank Effluent | 7.44 | 7.77 | - | pH-FTE-10 | MDE | Samples from last channels/final tank |  |  | 4.339% |  | pH (-)
10 | 2020-07-15 | 8:10 | Temperature | Final Tank Effluent | 23.9 | 24.7 | C | T-FTE-10 | MDE | Samples from last channels/final tank |  |  | 3.292% |  | Temperature (C)
10 | 2020-07-15 | 8:10 | Field TRC | Final Tank Effluent | 0.07 |  | mg/L | FTRC-FTE-10 | MDE | Samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
10 | 2020-07-15 | 7:42 | pH | CCT Effluent | 7.6 | 8.06 | - | pH-CCTE-10 | MDE | From small access hole at North end of the CCT's |  |  | 5.875% |  | pH (-)
10 | 2020-07-15 | 7:42 | Temperature | CCT Effluent | 24.1 | 24.7 | C | T-CCTE-10 | MDE | From small access hole at North end of the CCT's |  |  | 2.459% |  | Temperature (C)
10 | 2020-07-15 | 7:42 | Field TRC | CCT Effluent | 0.47 |  | mg/L | FTRC-CCTE-10 | MDE | From small access hole at North end of the CCT's |  |  |  |  | Field TRC (mg/L)
10 | 2020-07-15 | 9:05 | cBOD | Plant Influent | 170 |  | mg/L | cBOD-PI-10 | NYEnvironmental | Samples from screen No.2(the middle) |  |  |  |  | cBOD (mg/L)
10 | 2020-07-15 | 8:40 | cBOD | Primary Effluent | 140 |  | mg/L | cBOD-PE-10 | NYEnvironmental | Samples from trough No.2 (2nd from the ending |  |  |  |  | cBOD (mg/L)
10 | 2020-07-15 | 8:10 | cBOD | Final Tank Effluent | 4 |  | mg/L | cBOD-FTE-10 | NYEnvironmental | Samples from last channels/final tank |  | < |  |  | cBOD (mg/L)
10 | 2020-07-15 | 7:42 | cBOD | CCT Effluent | 4 |  | mg/L | cBOD-CCTE-10 | NYEnvironmental | From small access hole at North end of the CCT's |  | < |  |  | cBOD (mg/L)
10 | 2020-07-15 | 9:05 | Enterococcus | Plant Influent | 892500 |  | MPN/100mL | EC-PI-10 | NYEnvironmental | Samples from screen No.2(the middle) |  |  |  |  | Enterococcus (MPN/100mL)
10 | 2020-07-15 | 8:40 | Enterococcus | Primary Effluent | 307600 |  | MPN/100mL | EC-PE-10 | NYEnvironmental | Samples from trough No.2 (2nd from the ending |  |  |  |  | Enterococcus (MPN/100mL)
10 | 2020-07-15 | 8:10 | Enterococcus | Final Tank Effluent | 25600 |  | MPN/100mL | EC-FTE-10 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
10 | 2020-07-15 | 7:42 | Enterococcus | CCT Effluent | 10 |  | MPN/100mL | EC-CCTE-10 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | Enterococcus (MPN/100mL)
10 | 2020-07-15 | 8:10 | Enterococcus | Final Tank Effluent | 17950 |  | MPN/100mL | EC-FTE-10 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
10 | 2020-07-15 | 9:05 | Fecal Coliform | Plant Influent |  |  | MPN/100mL | FC-PI-10 | NYEnvironmental | Samples from screen No.2(the middle) VOID | X |  |  |  | Fecal Coliform (MPN/100mL)
10 | 2020-07-15 | 8:40 | Fecal Coliform | Primary Effluent |  |  | MPN/100mL | FC-PE-10 | NYEnvironmental | Samples from trough No.2 (2nd from the ending VOID | X |  |  |  | Fecal Coliform (MPN/100mL)
10 | 2020-07-15 | 8:10 | Fecal Coliform | Final Tank Effluent |  |  | MPN/100mL | FC-FTE-10 | NYEnvironmental | Samples from last channels/final tank VOID | X |  |  |  | Fecal Coliform (MPN/100mL)
10 | 2020-07-15 | 7:42 | Fecal Coliform | CCT Effluent |  |  | MPN/100mL | FC-CCTE-10 | NYEnvironmental | From small access hole at North end of the CCT's VOID | X |  |  |  | Fecal Coliform (MPN/100mL)
10 | 2020-07-15 | 8:10 | Fecal Coliform | Final Tank Effluent |  |  | MPN/100mL | FC-FTE-10 | NYEnvironmental | Samples from last channels/final tank VOID | X |  |  |  | Fecal Coliform (MPN/100mL)
10 | 2020-07-15 | 9:05 | TSS | Plant Influent | 130 |  | mg/L | TSS-PI-10 | NYEnvironmental | Samples from screen No.2(the middle) |  |  |  |  | TSS (mg/L)
10 | 2020-07-15 | 8:40 | TSS | Primary Effluent | 43 |  | mg/L | TSS-PE-10 | NYEnvironmental | Samples from trough No.2 (2nd from the ending |  |  |  |  | TSS (mg/L)
10 | 2020-07-15 | 8:10 | TSS | Final Tank Effluent | 6 |  | mg/L | TSS-FTE-10 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | TSS (mg/L)
10 | 2020-07-15 | 7:42 | TSS | CCT Effluent | 5.3 |  | mg/L | TSS-CCTE-10 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | TSS (mg/L)
11 | 2020-07-16 | 8:59 | pH | Plant Influent | 7.22 | 7.64 | - | pH-PI-11 | MDE | Samples from screen No.3(last from exit door) |  |  | 5.653% |  | pH (-)
11 | 2020-07-16 | 8:59 | Temperature | Plant Influent | 23.1 | 24.4 | C | T-PI-11 | MDE | Samples from screen No.3(last from exit door) |  |  | 5.474% |  | Temperature (C)
11 | 2020-07-16 | 8:59 | Field TRC | Plant Influent | 0.19 | 0.22 | mg/L | FTRC-PI-11 | MDE | Samples from screen No.3(last from exit door). Note that Khalid took 2 readings for TRC (0.19 and 0.22) at the plant influent as it was slightly elevated from earlier this week. |  |  | 14.63% |  | Field TRC (mg/L)
11 | 2020-07-16 | 8:30 | pH | Primary Effluent | 7.23 | 7.63 | - | pH-PE-11 | MDE | Samples from trough No.2 (3rd from the ending) |  |  | 5.384% |  | pH (-)
11 | 2020-07-16 | 8:30 | Temperature | Primary Effluent | 22.5 | 23.2 | C | T-PE-11 | MDE | Samples from trough No.2 (3rd from the ending) |  |  | 3.063% |  | Temperature (C)
11 | 2020-07-16 | 8:30 | Field TRC | Primary Effluent | 0 |  | mg/L | FTRC-PE-11 | MDE | Samples from trough No.2 (3rd from the ending) |  |  |  |  | Field TRC (mg/L)
11 | 2020-07-16 | 7:55 | pH | Final Tank Effluent | 7.44 | 7.84 | - | pH-FTE-11 | MDE | Samples from last channels/final tank |  |  | 5.236% |  | pH (-)
11 | 2020-07-16 | 7:55 | Temperature | Final Tank Effluent | 21.4 | 23.9 | C | T-FTE-11 | MDE | Samples from last channels/final tank |  |  | 11.04% |  | Temperature (C)
11 | 2020-07-16 | 7:55 | Field TRC | Final Tank Effluent | 0.02 |  | mg/L | FTRC-FTE-11 | MDE | Samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
11 | 2020-07-16 | 7:27 | pH | CCT Effluent | 7.54 | 8.06 | - | pH-CCTE-11 | MDE | From small access hole at North end of the CCT's |  |  | 6.667% |  | pH (-)
11 | 2020-07-16 | 7:27 | Temperature | CCT Effluent | 23.4 | 23.7 | C | T-CCTE-11 | MDE | From small access hole at North end of the CCT's |  |  | 1.274% |  | Temperature (C)
11 | 2020-07-16 | 7:27 | Field TRC | CCT Effluent | 0.52 |  | mg/L | FTRC-CCTE-11 | MDE | From small access hole at North end of the CCT's |  |  |  |  | Field TRC (mg/L)
11 | 2020-07-16 | 8:59 | cBOD | Plant Influent | 280 |  | mg/L | cBOD-PI-11 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | cBOD (mg/L)
11 | 2020-07-16 | 8:30 | cBOD | Primary Effluent | 92 |  | mg/L | cBOD-PE-11 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | cBOD (mg/L)
11 | 2020-07-16 | 7:55 | cBOD | Final Tank Effluent | 4 |  | mg/L | cBOD-FTE-11 | NYEnvironmental | Samples from last channels/final tank |  | < |  |  | cBOD (mg/L)
11 | 2020-07-16 | 7:27 | cBOD | CCT Effluent | 4 |  | mg/L | cBOD-CCTE-11 | NYEnvironmental | From small access hole at North end of the CCT's |  | < |  |  | cBOD (mg/L)
11 | 2020-07-16 | 8:59 | Enterococcus | Plant Influent | 902800 |  | MPN/100mL | EC-PI-11 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | Enterococcus (MPN/100mL)
11 | 2020-07-16 | 8:30 | Enterococcus | Primary Effluent | 365400 |  | MPN/100mL | EC-PE-11 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | Enterococcus (MPN/100mL)
11 | 2020-07-16 | 7:55 | Enterococcus | Final Tank Effluent | 67700 |  | MPN/100mL | EC-FTE-11 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
11 | 2020-07-16 | 7:27 | Enterococcus | CCT Effluent | 20.5 |  | MPN/100mL | EC-CCTE-11 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | Enterococcus (MPN/100mL)
11 | 2020-07-16 |  | Enterococcus | Final Tank Effluent | 55950 |  | MPN/100mL | EC-FTE-11 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Enterococcus (MPN/100mL)
11 | 2020-07-16 | 8:59 | Fecal Coliform | Plant Influent | 2310000 |  | MPN/100mL | FC-PI-11 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | Fecal Coliform (MPN/100mL)
11 | 2020-07-16 | 8:30 | Fecal Coliform | Primary Effluent | 2050000 |  | MPN/100mL | FC-PE-11 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | Fecal Coliform (MPN/100mL)
11 | 2020-07-16 | 7:55 | Fecal Coliform | Final Tank Effluent | 274000 |  | MPN/100mL | FC-FTE-11 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Fecal Coliform (MPN/100mL)
11 | 2020-07-16 | 7:27 | Fecal Coliform | CCT Effluent | 42.5 |  | MPN/100mL | FC-CCTE-11 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | Fecal Coliform (MPN/100mL)
11 | 2020-07-16 | 7:55 | Fecal Coliform | Final Tank Effluent | 205000 |  | MPN/100mL | FC-FTE-11 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | Fecal Coliform (MPN/100mL)
11 | 2020-07-16 | 8:59 | TSS | Plant Influent | 140 |  | mg/L | TSS-PI-11 | NYEnvironmental | Samples from screen No.3(last from exit door) |  |  |  |  | TSS (mg/L)
11 | 2020-07-16 | 8:30 | TSS | Primary Effluent | 44 |  | mg/L | TSS-PE-11 | NYEnvironmental | Samples from trough No.2 (3rd from the ending) |  |  |  |  | TSS (mg/L)
11 | 2020-07-16 | 7:55 | TSS | Final Tank Effluent | 6.5 |  | mg/L | TSS-FTE-11 | NYEnvironmental | Samples from last channels/final tank |  |  |  |  | TSS (mg/L)
11 | 2020-07-16 | 7:27 | TSS | CCT Effluent | 4 |  | mg/L | TSS-CCTE-11 | NYEnvironmental | From small access hole at North end of the CCT's |  |  |  |  | TSS (mg/L)
12 | 2020-07-17 | 9:36 | pH | Plant Influent | 7.35 | 7.67 | - | pH-PI-12 | MDE | Samples from screen No.1(First from exit door) |  |  | 4.261% |  | pH (-)
12 | 2020-07-17 | 9:36 | Temperature | Plant Influent | 22.7 | 24.8 | C | T-PI-12 | MDE | Samples from screen No.1(First from exit door) |  |  | 8.842% |  | Temperature (C)
12 | 2020-07-17 | 9:36 | Field TRC | Plant Influent | 0.17 |  | mg/L | FTRC-PI-12 | MDE | Samples from screen No.1(First from exit door) |  |  |  |  | Field TRC (mg/L)
12 | 2020-07-17 | 8:58 | pH | Primary Effluent | 7.13 | 7.45 | - | pH-PE-12 | MDE | Samples from trough No.2 (2nd from the ending) |  |  | 4.39% |  | pH (-)
12 | 2020-07-17 | 8:58 | Temperature | Primary Effluent | 22.9 | 23.3 | C | T-PE-12 | MDE | Samples from trough No.2 (2nd from the ending) |  |  | 1.732% |  | Temperature (C)
12 | 2020-07-17 | 8:58 | Field TRC | Primary Effluent | 0.04 |  | mg/L | FTRC-PE-12 | MDE | Samples from trough No.2 (2nd from the ending) |  |  |  |  | Field TRC (mg/L)
12 | 2020-07-17 | 8:30 | pH | Final Tank Effluent | 7.53 | 7.88 | - | pH-FTE-12 | MDE | Samples from last channels/final tank |  |  | 4.543% |  | pH (-)
12 | 2020-07-17 | 8:30 | Temperature | Final Tank Effluent | 24 | 24.1 | C | T-FTE-12 | MDE | Samples from last channels/final tank |  |  | 0.4158% |  | Temperature (C)
12 | 2020-07-17 | 8:30 | Field TRC | Final Tank Effluent | 0.04 |  | mg/L | FTRC-FTE-12 | MDE | Samples from last channels/final tank |  |  |  |  | Field TRC (mg/L)
12 | 2020-07-17 | 7:50 | pH | CCT Effluent | 7.53 | 8.07 | - | pH-CCTE-12 | MDE | From small access hole at North end of the CCT's |  |  | 6.923% |  | pH (-)
12 | 2020-07-17 | 7:50 | Temperature | CCT Effluent | 23.6 | 23.8 | C | T-CCTE-12 | MDE | From small access hole at North end of the CCT's |  |  | 0.8439% |  | Temperature (C)
12 | 2020-07-17 | 7:50 | Field TRC | CCT Effluent | 0.48 |  | mg/L | FTRC-CCTE-12 | MDE | From small access hole at North end of the CCT's |  |  |  |  | Field TRC (mg/L)
12 | 2020-07-17 |  | cBOD | Plant Influent | 200 |  | mg/L | cBOD-PI-12 | NYEnvironmental | [5 empty] | cBOD (mg/L)
12 | 2020-07-17 |  | cBOD | Primary Effluent | 180 |  | mg/L | cBOD-PE-12 | NYEnvironmental | [5 empty] | cBOD (mg/L)
12 | 2020-07-17 |  | cBOD | Final Tank Effluent | 4 |  | mg/L | cBOD-FTE-12 | NYEnvironmental |  |  | < |  |  | cBOD (mg/L)
12 | 2020-07-17 |  | cBOD | CCT Effluent | 4 |  | mg/L | cBOD-CCTE-12 | NYEnvironmental |  |  | < |  |  | cBOD (mg/L)
12 | 2020-07-17 | 9:36 | Enterococcus | Plant Influent | 984000 |  | MPN/100mL | EC-PI-12 | NYEnvironmental | [5 empty] | Enterococcus (MPN/100mL)
12 | 2020-07-17 | 8:58 | Enterococcus | Primary Effluent | 410600 |  | MPN/100mL | EC-PE-12 | NYEnvironmental | [5 empty] | Enterococcus (MPN/100mL)
12 | 2020-07-17 | 8:30 | Enterococcus | Final Tank Effluent | 35600 |  | MPN/100mL | EC-FTE-12 | NYEnvironmental | [5 empty] | Enterococcus (MPN/100mL)
12 | 2020-07-17 | 7:50 | Enterococcus | CCT Effluent | 10 |  | MPN/100mL | EC-CCTE-12 | NYEnvironmental | [5 empty] | Enterococcus (MPN/100mL)
12 | 2020-07-17 | 8:30 | Enterococcus | Final Tank Effluent | 40650 |  | MPN/100mL | EC-FTE-12 | NYEnvironmental | [5 empty] | Enterococcus (MPN/100mL)
12 | 2020-07-17 | 9:36 | Fecal Coliform | Plant Influent | 6530000 |  | MPN/100mL | FC-PI-12 | NYEnvironmental | [5 empty] | Fecal Coliform (MPN/100mL)
12 | 2020-07-17 | 8:58 | Fecal Coliform | Primary Effluent | 324000 |  | MPN/100mL | FC-PE-12 | NYEnvironmental | not typical of primary effluent fecal |  |  |  | Potential Outlier | Fecal Coliform (MPN/100mL)
12 | 2020-07-17 | 8:30 | Fecal Coliform | Final Tank Effluent | 560000 |  | MPN/100mL | FC-FTE-12 | NYEnvironmental | [5 empty] | Fecal Coliform (MPN/100mL)
12 | 2020-07-17 | 7:50 | Fecal Coliform | CCT Effluent | 72 |  | MPN/100mL | FC-CCTE-12 | NYEnvironmental | [5 empty] | Fecal Coliform (MPN/100mL)
12 | 2020-07-17 | 8:30 | Fecal Coliform | Final Tank Effluent | 650000 |  | MPN/100mL | FC-FTE-12 | NYEnvironmental | [5 empty] | Fecal Coliform (MPN/100mL)
12 | 2020-07-17 |  | TSS | Plant Influent | 170 |  | mg/L | TSS-PI-12 | NYEnvironmental | [5 empty] | TSS (mg/L)
12 | 2020-07-17 |  | TSS | Primary Effluent | 46 |  | mg/L | TSS-PE-12 | NYEnvironmental | [5 empty] | TSS (mg/L)
12 | 2020-07-17 |  | TSS | Final Tank Effluent | 5 |  | mg/L | TSS-FTE-12 | NYEnvironmental |  |  | < |  |  | TSS (mg/L)
12 | 2020-07-17 |  | TSS | CCT Effluent | 4 |  | mg/L | TSS-CCTE-12 | NYEnvironmental | [5 empty] | TSS (mg/L)
1 | 2020-06-29 |  | Cylinder Reading Average | Aeration Tank Effluent | 450 |  | mL/L | CRA-ATE-01 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
2 | 2020-06-30 |  | Cylinder Reading Average | Aeration Tank Effluent | 313 |  | mL/L | CRA-ATE-02 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
3 | 2020-07-01 |  | Cylinder Reading Average | Aeration Tank Effluent | 343 |  | mL/L | CRA-ATE-03 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
4 | 2020-07-07 |  | Cylinder Reading Average | Aeration Tank Effluent | 170 |  | mL/L | CRA-ATE-04 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
5 | 2020-07-08 |  | Cylinder Reading Average | Aeration Tank Effluent | 330 |  | mL/L | CRA-ATE-05 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
6 | 2020-07-09 |  | Cylinder Reading Average | Aeration Tank Effluent | 223 |  | mL/L | CRA-ATE-06 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
7 | 2020-07-10 |  | Cylinder Reading Average | Aeration Tank Effluent | 128 |  | mL/L | CRA-ATE-07 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
8 | 2020-07-13 |  | Cylinder Reading Average | Aeration Tank Effluent | 85 |  | mL/L | CRA-ATE-08 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
9 | 2020-07-14 |  | Cylinder Reading Average | Aeration Tank Effluent | 90 |  | mL/L | CRA-ATE-09 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
10 | 2020-07-15 |  | Cylinder Reading Average | Aeration Tank Effluent | 98 |  | mL/L | CRA-ATE-10 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
11 | 2020-07-16 |  | Cylinder Reading Average | Aeration Tank Effluent | 88 |  | mL/L | CRA-ATE-11 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
12 | 2020-07-17 |  | Cylinder Reading Average | Aeration Tank Effluent | 60 |  | mL/L | CRA-ATE-12 | Plant | [5 empty] | Cylinder Reading Average (mL/L)
1 | 2020-06-29 |  | MLSS | Aeration Tank Effluent | 1160 |  | mg/L | MLSS-ATE-01 | Plant | [5 empty] | MLSS (mg/L)
2 | 2020-06-30 |  | MLSS | Aeration Tank Effluent | 1070 |  | mg/L | MLSS-ATE-02 | Plant | [5 empty] | MLSS (mg/L)
3 | 2020-07-01 |  | MLSS | Aeration Tank Effluent | 980 |  | mg/L | MLSS-ATE-03 | Plant | [5 empty] | MLSS (mg/L)
4 | 2020-07-07 |  | MLSS | Aeration Tank Effluent | 1020 |  | mg/L | MLSS-ATE-04 | Plant | [5 empty] | MLSS (mg/L)
5 | 2020-07-08 |  | MLSS | Aeration Tank Effluent | 780 |  | mg/L | MLSS-ATE-05 | Plant | [5 empty] | MLSS (mg/L)
6 | 2020-07-09 |  | MLSS | Aeration Tank Effluent | 670 |  | mg/L | MLSS-ATE-06 | Plant | [5 empty] | MLSS (mg/L)
7 | 2020-07-10 |  | MLSS | Aeration Tank Effluent | 560 |  | mg/L | MLSS-ATE-07 | Plant | [5 empty] | MLSS (mg/L)
8 | 2020-07-13 |  | MLSS | Aeration Tank Effluent | 770 |  | mg/L | MLSS-ATE-08 | Plant | [5 empty] | MLSS (mg/L)
9 | 2020-07-14 |  | MLSS | Aeration Tank Effluent | 765 |  | mg/L | MLSS-ATE-09 | Plant | [5 empty] | MLSS (mg/L)
10 | 2020-07-15 |  | MLSS | Aeration Tank Effluent | 760 |  | mg/L | MLSS-ATE-10 | Plant | [5 empty] | MLSS (mg/L)
11 | 2020-07-16 |  | MLSS | Aeration Tank Effluent | 770 |  | mg/L | MLSS-ATE-11 | Plant | [5 empty] | MLSS (mg/L)
12 | 2020-07-17 |  | MLSS | Aeration Tank Effluent | 780 |  | mg/L | MLSS-ATE-12 | Plant | [5 empty] | MLSS (mg/L)
1 | 2020-06-29 |  | SVI | Aeration Tank Effluent | 387.931 |  | mL/g | SVI-ATE-01 | Plant | [5 empty] | SVI (mL/g)
2 | 2020-06-30 |  | SVI | Aeration Tank Effluent | 292.5234 |  | mL/g | SVI-ATE-02 | Plant | [5 empty] | SVI (mL/g)
3 | 2020-07-01 |  | SVI | Aeration Tank Effluent | 350 |  | mL/g | SVI-ATE-03 | Plant | [5 empty] | SVI (mL/g)
4 | 2020-07-07 |  | SVI | Aeration Tank Effluent | 166.6667 |  | mL/g | SVI-ATE-04 | Plant | [5 empty] | SVI (mL/g)
5 | 2020-07-08 |  | SVI | Aeration Tank Effluent | 423.0769 |  | mL/g | SVI-ATE-05 | Plant | [5 empty] | SVI (mL/g)
6 | 2020-07-09 |  | SVI | Aeration Tank Effluent | 332.8358 |  | mL/g | SVI-ATE-06 | Plant | [5 empty] | SVI (mL/g)
7 | 2020-07-10 |  | SVI | Aeration Tank Effluent | 228.5714 |  | mL/g | SVI-ATE-07 | Plant | [5 empty] | SVI (mL/g)
8 | 2020-07-13 |  | SVI | Aeration Tank Effluent | 110.3896 |  | mL/g | SVI-ATE-08 | Plant | [5 empty] | SVI (mL/g)
9 | 2020-07-14 |  | SVI | Aeration Tank Effluent | 117.6471 |  | mL/g | SVI-ATE-09 | Plant | [5 empty] | SVI (mL/g)
10 | 2020-07-15 |  | SVI | Aeration Tank Effluent | 128.9474 |  | mL/g | SVI-ATE-10 | Plant | [5 empty] | SVI (mL/g)
11 | 2020-07-16 |  | SVI | Aeration Tank Effluent | 114.2857 |  | mL/g | SVI-ATE-11 | Plant | [5 empty] | SVI (mL/g)
12 | 2020-07-17 |  | SVI | Aeration Tank Effluent | 76.9231 |  | mL/g | SVI-ATE-12 | Plant | [5 empty] | SVI (mL/g)
1 | 2020-06-29 | 8:00 | Flow | Plant Influent | 22 |  | MGD | Flow-PI-01 | Plant | [5 empty] | Flow (MGD)
2 | 2020-06-30 | 8:00 | Flow | Plant Influent | 20 |  | MGD | Flow-PI-02 | Plant | [5 empty] | Flow (MGD)
3 | 2020-07-01 | 8:00 | Flow | Plant Influent | 21 |  | MGD | Flow-PI-03 | Plant | [5 empty] | Flow (MGD)
4 | 2020-07-07 | 8:00 | Flow | Plant Influent | 31 |  | MGD | Flow-PI-04 | Plant | [5 empty] | Flow (MGD)
5 | 2020-07-08 | 8:00 | Flow | Plant Influent | 21 |  | MGD | Flow-PI-05 | Plant | [5 empty] | Flow (MGD)
6 | 2020-07-09 | 8:00 | Flow | Plant Influent | 20 |  | MGD | Flow-PI-06 | Plant | [5 empty] | Flow (MGD)
7 | 2020-07-10 | 8:00 | Flow | Plant Influent | 20 |  | MGD | Flow-PI-07 | Plant | [5 empty] | Flow (MGD)
8 | 2020-07-13 | 8:00 | Flow | Plant Influent | 25 |  | MGD | Flow-PI-08 | Plant | [5 empty] | Flow (MGD)
9 | 2020-07-14 | 8:00 | Flow | Plant Influent | 19 |  | MGD | Flow-PI-09 | Plant | [5 empty] | Flow (MGD)
10 | 2020-07-15 | 8:00 | Flow | Plant Influent | 18 |  | MGD | Flow-PI-10 | Plant | [5 empty] | Flow (MGD)
11 | 2020-07-16 | 8:00 | Flow | Plant Influent | 19 |  | MGD | Flow-PI-11 | Plant | [5 empty] | Flow (MGD)
12 | 2020-07-17 | 8:00 | Flow | Plant Influent | 26 |  | MGD | Flow-PI-12 | Plant | [5 empty] | Flow (MGD)
Formulas:
Sampling Dates = WORKDAY(C1,Table5[[#This Row],[Day]]-1,Table4[Skipdays])